## Sheet1
Cape Cod Commission 91-001, April 1992 | [11 empty] | Instructions
Nitrogen Loading Calculations | [11 empty] | These calculations have been modified for the Brewster Zoning Bylaw
Target Concentration |  |  |  | 5 | ppm
Wastewater
| Residential |  |  | 35 | ppm | [6 empty] | These are the assumed concentrations of total nitrogen in the wastewater
| Nonresidential |  |  | 35 | ppm | [6 empty] | These are the assumed concentrations of total nitrogen in the wastewater
Occupancy
| Range | 3 | people per unit | 2 | people per bedroom | [6 empty] | These are the varied occupancy rates between 2.5 and full Title 5 occupancy
Lawns
| Area |  |  | 5000 | S.F. | [6 empty] | Under the Cape Cod Commission, there is a presumed 5,000 S.F. of fertilized lawn. There is nothing in the Bylaw that says to vary.
| Fertilizer |  |  | 2 | lbs./1000 S.F. | [6 empty] | Under the Bylaw, there is a presumption of 2 lb./1000 S.F. Under the CCC, it is presumed at 3 lbs./1000 S.F.
| Leaching |  |  | 25% | [7 empty] | Assumed leaching under the CCC.
Background |  |  |  | 0.05 | ppm | [6 empty] | Under the CCC, there is no assumption of background Nitrogen. Under the Bylaw, there's 0.05 ppm.
Recharge
| Off impervious surfaces |  |  | 40 | in/year | [6 empty] | Recharge from the CCC.
Concentrations
|  | Road Runoff |  | 1.5 | ppm | [6 empty] | Concentrations in the CCC and the Bylaw match.
|  | Roof Runoff |  | 0.75 | ppm | [6 empty] | Concentrations in the CCC and the Bylaw match.
Natural Areas
|  | Brewster |  | 17 | in/year | [6 empty] | Natural recharge in Brewster from the CCC.
Residential Nitrogen Loading | [11 empty] | Here is where you actually input numbers.
Town |  | Brewster |  | 17 | in/year | [6 empty] | If you were working in another Town, you would find the reacharge of that Town.
Homesize |  |  |  | 5 | Bedrooms |  | Treated? | no | (Yes or No) |  |  | Input the number of bedrooms and Yes/No if the effluent is treated (35 ppm vs 19 ppm)
Lot Size |  | 33100 | S.F. | 0.75987 | acre | [6 empty] | Input the lot size in S.F.
Impervious Roof |  | 2500 | S.F. | 0.057392 | acre | [6 empty] | Input the impervious roof in S.F.
Impervious Paving |  | 3000 | S.F. | 0.068871 | acre | [6 empty] | Input the driveway / coverage in S.F.
Lawn Area |  | 5000 | S.F. | 0.11478 | acre | [6 empty] | If you want to modify the lawn area, this is where you can input it in S.F.
Pervious Area |  | 27600 | S.F. | 0.63361 | acre | [6 empty] | This is calculated.
Title 5 Flow | [11 empty] | All of these numbers come out of the above inputs.
5 | bedrooms | 110 | gpd/bedroom | 3.785 | L/gal | 2081.75 | L/d | 35 | mg/L | 72861.25 | mg/d
Actual Occupancy
3 | people per unit | 55 | gpd/person | 3.785 | L/gal | 624.525 | L/d | 35 | mg/L | 21858.375 | mg/d
Impervious Surfaces
2500 | roof | 0.0091324 | ft/day | 28.32 | L/CF | 646.5753 | L/d | 0.75 | mg/L | 484.9315 | mg/d
3000 | road | 0.0091324 | ft/day | 28.32 | L/CF | 775.8904 | L/d | 1.5 | mg/L | 1163.8356 | mg/d
Lawn
5000 | lawn |  |  | 25% | Leaching |  |  | 2.4877 | mg/SF / day | 3109.589 | mg/d
Natural
27600 | natural | 0.0038813 | ft/year | 28.32 | L/CF | 3033.7315 | L/d
Background
Runoff |  | 4456.1973 | L/d | 0.05 | ppm |  |  |  |  | 222.8099 | mg/d
Summary
Title 5 Flow |  | 6537.9473 | L/d | 77842.416 | mg/d | 11.9062 | ppm
Actual Occupancy |  | 5080.7223 | L/d | 26839.541 | mg/d | 5.2826 | ppm
Average nitrogen load | [5 empty] | 8.5944 | ppm |  |  |  |  | This is the final average.